## PART 1	GENERAL

  - SUMMARY

    - This section includes vertical copper fin-tube non-condensing hot water boiler(s) for outdoor space-heating application.

  - REFERENCES

    - Underwriters Laboratories

      - UL 795: Commercial-Industrial Gas Heating Equipment

    - American Society of Mechanical Engineers

      - ASME Section IV: Boiler and Pressure Vessel Code - Heating Boilers

      - ASME CSD-1: Controls and Safety Devices for Automatically Fired Boilers

    - American Society of Heating, Refrigeration and Air Conditioning Engineers

      - ASHRAE: Standard 90.1 Energy Standard for Buildings

    - American National Standards Institute

      - ANSI Z21.13: Gas Fired Low Pressure Steam and Hot Water Boilers

    - Hydronics Institute, Division of Air Conditioning, Heating and Refrigeration Institute:

      - BTS-2000: Testing Standard to Determine Efficiency of Commercial Space Heating Boilers

    - National Fire Protection Association

      - NFPA 54: National Fuel Gas Code (ANSI Z223.1)

    - Relevant local and/or project specific Codes and Standards

  - SUBMITTALS

    - In accordance with Contract Documents. Minimum product data to include:

      - Capacities, accessories and options included with boiler.

      - General layout, dimensions, size and location of all required connections.

      - Electrical characteristics -provide wiring diagrams that are specific to this project.

      - Weight and mounting loads.

      - Manufacturer's installation and start-up instructions.

      - Equipment Operation and Maintenance Manuals and control device cut-sheets.

  - QUALITY ASSURANCE

    - Use an adequate number of skilled workers, trained and experienced in the necessary crafts, and who are completely familiar with the specified requirements, pertinent contract documents, and methods needed for proper performance of the work described therein.

    - Provide the services of a manufacturer's factory-authorized representative to inspect and verify proper installation of this equipment, and to provide equipment start-up and operator training.

  - DELIVERY, STORAGE, AND HANDLING

    - In accordance with Contract Documents.

    - Accept equipment and accessories in Factory shipping packaging. Inspect for damage. Keep boiler in a vertical position from time of delivery to final installation.

    - While stored, all equipment must be protected from external elements such as inclement weather, job site construction activity, etc. Protect equipment from damage by leaving packaging in place until installation.

  - WARRANTY

    - The boiler shall come with the warranties stated below. Warranty period shall be one (1) year from date of start-up or eighteen (18) months from date of shipment, whichever comes first.

      - Heat exchanger: 5-year limited warranty, and a 20-year warranty against thermal shock.

      - Burner: 10-year limited warranty.

      - All other parts: 1-year limited warranty.

PART 2	PRODUCTS

  - ACCEPTABLE MANUFACTURERS

- Thermal Solutions Boiler, Evolution Model EVOM [500, 750, 1000, 1500, 2000] or approved equal.  Refer to the Equipment Schedule in the Contract Documents for specific design and performance criteria.

- It shall be the responsibility of the Contractor to insure that any substituted equipment is equivalent in fit, form and function to the specified equipment. The cost of any additional work caused by the substitution of equipment shall be borne by the Contractor.

- Or approved equal.

  - GENERAL REQUIREMENTS

A.	Boiler

  - The boiler shall be a factory-packaged unit, complete with jacket, gas manifold, burner and controls mounted and wired, as specified in this Section. The boiler shall be factory assembled and fire tested. Boiler connections shall be limited to the water supply & return, relief valve and boiler drains, fuel, electrical power, exhaust vent and air inlet (as specified/shown in contract documents).

  - The boiler shall be constructed in conformance to ASME Section IV and UL 795. The boiler shall bear the ASME “H” stamp and be National Board Listed for 160 psi working pressure and 250F. The gas train and safety controls shall conform to requirements of UL 795 and ASME CSD-1.

  - The complete boiler shall be factory fire tested by the manufacturer and a copy of the fire-test report shall be supplied with the boiler.

      - The boiler heat exchanger shall be constructed in accordance with Section IV of the ASME code with straight copper tubes having extruded, integral fins. Fin spacing shall be at least seven (7) fins per inch. Copper tubes shall have a minimum wall thickness of .072”. Tubes shall be rolled securely into the headers (top and bottom). There shall be no bolts, gaskets, “O-Rings”, welding or brazing used in the header construction. Removable access plugs shall be included in the design of the heat exchanger to allow for access (cleaning and inspection) and replacement of each individual tube. The heat exchanger shall encompass the entire burner and be enclosed in stainless steel inner shells. The heat exchanger shall be of sufficient size and design to ensure effective, non-limiting control of the water flow rate and velocity through each tube at all load levels. The heating surface of the heat exchanger shall be no less than 6.5 ft2 per boiler horsepower.

      - The boiler shall be contained in a minimum 16-gauge negative pressure aluminized steel jacket protected with a UV resistant powder-coated finish. The jacket panels must be lockable to prevent unauthorized tampering of control devices. The boiler control panel shall be non-pressurized allowing boiler operation with any jacket panels removed. Hinge-less front and rear access panels shall be provided for easy access to the operating controls and to eliminate electric code “swing radius” clearance issues.

      - The operating sound level of the boiler shall not exceed 50 dBA.

      - Electrical input to the boiler shall be [120v/1ph, 208v/1ph, 230v/1ph, 208v/3ph, 230v/3ph, 460v/3ph]. The manufacturer will mount the control transformer and fuses inside the boiler control panel. Single-point electrical hook-up for each boiler shall be provided. Separate power wiring and control wiring is not acceptable. The boiler must utilize a commercial grade 120v/1ph control system.  A residential type 24v control system is not acceptable. A dedicated disconnect shall be provided for the boiler.

- B.	Combustion System

      - The burner shall be a radiant non-corroding ceramic burner, with no moving parts. Double-meshed screen, fiber-metal mats, aluminized or stainless steel construction of the burner will not be accepted. The burner shall fire in a full 360 degree pattern providing uniform heat transfer across the entire heat exchanger. A viewing port shall be provided for visual observation of burner performance. Burner shall require no maintenance, inspection or service.

      - Burner operation shall provide infinite Modulation with minimum 3:1 turn down utilizing a Variable Frequency Drive and air-fuel ratio control gas valve for dependable, repeatable modulation and precise combustion control. The boiler will be equipped with a non-sparking blower manufactured with a cast-aluminum housing. Dampers, linkages or a single-speed fan are not acceptable.

      - An interrupted-type mixed fuel/air pilot system with electric spark-to-pilot ignition shall be used. The pilot system shall use a UV scanner to prove pilot prior to energizing the main gas valves.  Hot surface ignition systems and flame rods are not acceptable.

      - The entire ignition and firing control sequence shall be monitored by a UL approved commercial-type microprocessor based integrated flame safeguard burner control with first out fault annunciation and operating sequence and diagnostic indicator lights. The burner control shall incorporate both pre-purge and post-purge timing functions.  In the event of ignition pilot and/or main flame failure a burner “lockout” will occur requiring a manual reset of the burner control.  It shall also recognize the Proof of Closure switches on the gas valves (if DB&B w/POC).

      - The combustion air blower shall be equipped with a replaceable combustion air filter, 99% efficient to one micron to protect the burner from contamination. A delta-P type pressure switch shall be provided to alert the boiler operator of a dirty filter condition. Air inlet dampers and vacuum relief dampers are not required for proper operation. A combustion air flow switch shall be provided.

      - The gas train shall be UL/FM/CSD-1 compliant and certified to take a maximum of 5 psi Natural Gas [2 psi Propane (LPG)]. Additional step-down regulators are not allowed. The gas train shall consist of a pilot gas pressure regulator, high and low gas pressure switches (with manual reset), automatic main and redundant gas valve - Motorized automatic main and redundant gas valve and a normally open vent valve in between (if DB&B) - Motorized automatic main and redundant gas valve w/ Proof of Closure contacts and a normally open vent valve in between (if DB&B w/POC), leak test valves downstream of each gas valve, a manual shut off valve upstream of burner and downstream of last gas valve. The main gas valve shall perform the functions of safety shutoff, constant pressure regulation and air-fuel ratio control.

- C.	Operating Control

- 1.	The boiler shall be equipped with a microprocessor based Temperature Controller to control burner firing rate modulation in response to boiler heat load. A temperature sensor shall be located in the outlet side of the heat exchanger to provide the input signal to the Temperature Controller. The output signal from the Temperature Controller shall vary the blower speed via the Variable Frequency Drive. The Temperature Controller shall have a user-friendly menu that allows easy selection of desired operating temperature, upper and lower temperature set-point limits, burner on/off thresholds, PID control loop characteristics and local or remote operating modes. The Temperature Controller shall have an outdoor temperature reset function to allow the boiler operating temperature to vary based on outdoor ambient temperature. The Temperature Controller shall be capable of accepting either a 0-10 vdc or 4-20 mA remote signal for changing temperature set-points and/or remote modulation control. The control system shall be capable of communicating with a BAS/BMS using Modbus communication protocol.

- D.	Water Trim

- Water trim devices including an ASME rated pressure relief valve set at 125 [30, 50, 60, 75, 100, 150] psig, combination water pressure and temperature gage (furnish graduated pressure gauge scale from 1-1/2 to 3 times of pressure relief valve setting) and water flow switch to prevent burner operation during low water flow conditions shall be provided in the boiler outlet piping. An adjustable high limit temperature controller with manual reset to prevent water temperature from exceeding a safe system temperature and an Auxiliary Low Water Cutoff to provide redundant low water protection shall both be provided.

- E.	Vent & Intake Air Connections

- The boiler shall be designed to accommodate sealed, direct, or conventional venting options. The flue duct shall be AL 29-4C, positive pressure type vent material.  Single wall vent is acceptable where allowed by local code.

- Barometric dampers are to be used only on multiple boiler installations where the individual vents are combined into a common vent.

- When used for sealed combustion, air intake piping can be PVC or galvanized smoke pipe that is sealed and pressure tight. Pipe must be at least the same size as the air inlet connection on the boiler.

- Intake dampers and vacuum relief dampers are not required for sealed combustion/direct venting.  Vacuum relief dampers can violate the intent of sealed combustion/direct vent applications.

2.3	PERFORMANCE

- Boiler efficiency shall be as stated in the Equipment Schedule of the Contract Documents.

- The burner shall emit no more than 9 ppm NOx and 50 ppm CO (corrected to 3% O2) at all firing rates.

- Provide services of a manufacturer's authorized representative to perform combustion test including boiler firing rate, gas flow rate, heat input, burner manifold gas pressure, percent carbon monoxide, percent oxygen, percent excess air, flue gas temperature at outlet, ambient temperature, net stack temperature, percent stack loss, percent combustion efficiency, and heat output.  Perform test at minimum, mid-range, and high fire.

PART 3	EXECUTION

- 3.1	INSTALLATION

- In accordance with Contract Documents and boiler manufacturer's printed instructions.

- Flush and clean boilers upon completion of installation in accordance with manufacturer's start-up instructions. The boiler must be isolated when any cleaning or testing of system piping is being performed.

- Install skid plumb and level, to plus or minus 1/16 inch over base.

- Maintain manufacturer's recommended clearances around and over equipment, and as required by local Code.

- Arrange all electrical conduit, piping, exhaust vent, and air intake with clearances for burner removal and service of all equipment.

- Connect full size exhaust vent to boiler vent connection.

- If shown in Contract Drawings, connect full sized air inlet vent to flanged connector on boiler.

- Connect fuel piping in accordance with NFPA 54. Pipe size to be the same, or greater, than the gas train inlet connection.

- Use full size (minimum) pipe/tubing on all gas vent connections.

- Connect water piping, full size, to water supply and return connections.

- Install all piping accessories per the details on the Contract Documents.

- Install discharge piping from relief valves (open termination for viewing) and all drains to nearest floor drain.

- Provide necessary water treatment to satisfy manufacturer’s specified water quality limits.

- END OF SECTION