## Buffer Tank Sizing Calcs
BUFFER TANK SIZING CALCULATION
H2OMax Buffer tank - 26 - 119 gallons |  |  | Thermal Solutions Buffer Tank 40 to 860 gallons
Information needed:
| - Run time* |  | 10 | minutes
| - Minimum boiler output |  | 150000 | btuh
| - Minimum system load |  | 75000 | btuh
| - System delta T |  | 20 | °F
*Minimum boiler run time of 10 minutes is recommended
Formula:
(Run time x (Minimum boiler output – Minimum system load))
(System delta T x 8.33 weight of 1 gallon water x 60 min)
|  | Based on the above data, you would need a | 75 | gallon buffer tank

## Is Buffer Tank Needed
BUFFER TANK SIZING CALCULATION
1
H2OMax Buffer tank - 26 - 119 gallons |  |  | Thermal Solutions Buffer Tank 40 to 860 gallons
Boiler(s) Water Volume: |  |  | 16.2 | gallons | 10
Qty: |  |  | 2
Boiler Turndown |  |  | 10 | :1
System Water Volume: |  |  | 50 | gallons
Information needed:
| - Run time* |  | 10 | minutes
| - Minimum boiler output |  | 97000 | btuh
| - Minimum system load |  | 100000 | btuh
| - System delta T |  | 20 | °F
*Minimum boiler run time of 10 minutes is recommended
Formula:
(Run time x (Minimum boiler output – Minimum system load))
(System delta T x 8.33 weight of 1 gallon water x 60 min)
|  | System + Boiler Volume = | 66.2 | gallons
|  | Based on the above data, you would need | 0 | gallons to prevent boiler cycling

## Sheet2 (hidden)
ID | Product Sizes | Water Volume (Gallons) | Turndown | Output | Min Output
1 | APX-425C | 3.4 | 5 | 375000 | 75000
2 | APX-525C | 4.3 | 5 | 485000 | 97000
3 | APX-625C | 5.4 | 5 | 594000 | 118800
4 | APX-725C | 5.4 | 5 | 689000 | 137800
5 | APX-825C | 6.2 | 5 | 760000 | 152000
6 | AMP-400 | 3.8 | 10 | 388000 | 38800
7 | AMP-500 | 4.3 | 10 | 485000 | 48500
8 | AMP-650 | 5.6 | 10 | 631000 | 63100
9 | AMP-800 | 6.6 | 10 | 776000 | 77600
10 | AMP-1000L | 8.1 | 10 | 970000 | 97000
11 | AMP-1000 | 12 | 5 | 970000 | 194000
12 | AMP-1250 | 12 | 5 | 1213000 | 242600
13 | AMP-1500 | 13.9 | 5 | 1455000 | 291000
14 | AMP-2000 | 17.2 | 5 | 1940000 | 388000
15 | AMP-2500 | 36.4 | 5 | 2425000 | 485000
16 | AMP-3000 | 36.4 | 5 | 2910000 | 582000
17 | AMP-3500 | 47.1 | 5 | 3395000 | 679000
18 | AMP-4000 | 47.1 | 5 | 3880000 | 776000
19 | ARC-1000 | 19.7 | 5 | 950000 | 190000
20 | ARC-1500 | 27.3 | 5 | 1425000 | 285000
21 | ARC-2000 | 27.3 | 5 | 1900000 | 380000
22 | ARC-2500 | 39.3 | 5 | 2375000 | 475000
23 | ARC-3000 | 39.3 | 5 | 2850000 | 570000
24 | ARC-3500 | 56.1 | 20 | 3325000 | 166250
25 | ARC-4000 | 56.1 | 20 | 3800000 | 190000
26 | ARC-4500 | 80.9 | 20 | 4275000 | 213750
27 | ARC-5000 | 80.9 | 20 | 4750000 | 237500
28 | ARC-5500 | 80.9 | 20 | 5225000 | 261250
29 | ARC-6000 | 80.9 | 20 | 5700000 | 285000
30 | EV-500 | 6.1 | 3 | 431000 | 143666.6667
31 | EV-750 | 15.9 | 3 | 623000 | 207666.6667
32 | EV-1000 | 16.4 | 3 | 819000 | 273000
33 | EV-1500 | 17.4 | 3 | 1251000 | 417000
34 | EV-2000 | 18.5 | 3 | 1696000 | 565333.3333
35 | EV-2000S | 40.1 | 3 | 1732000 | 577333.3333
36 | EV-2500 | 41.6 | 3 | 2170000 | 723333.3333
37 | EV-3000 | 43.1 | 3 | 2610000 | 870000